## Slide 1
Module 1: Physical Processes in Electric Utilities
Topic 1.2 Wind Energy Grid Integration
Manohar Chamana, Ph.D.
Instructor
National Wind Institute
Texas Tech University

## Slide 2: Subtopics Covered
Wind Turbine Conversion Principles
Wind Turbine Mechanical System
Wind Turbine Electrical System
Wind Energy Grid Integration and Operation

## Slide 3: Wind Turbine Principles
Converting one form of energy to another
Kinetic Energy
Mechanical Energy
Electrical Energy
Overall: 42 – 50% Efficient Today… Theoretical Maximum is 59.3% (no losses)
Component | Rotor | Gearbox | Generator | Converter
Efficiency | 45-52% | 95-97% | 97-98% | 96-99%
3
Notes: 3
The basic functional principle of a wind turbine generation system concerns the conversion of kinetic (movement) energy of the wind into electrical energy.
This is done in two stages:
Kinetic energy  mechanical energy  electrical energy
The energy of the wind sets the rotor of the WTGS into motion.
The rotor is connected to the rotor shaft via the hub. The gearbox converts the slow rotational speed of the rotor shaft into a higher speed for the generator.
Finally, the generator converts the mechanical energy into electrical power.
The energy converters of a wind turbine generation system are thus the rotor and the generator.

## Slide 4: Why can’t we extract ALL the power in the wind?

## Slide 5: How much wind power do we extract?
Notes: Mechanical Energy available in Blue
Power Curve in Pink

## Slide 6: Wind turbine components

## Slide 7
Wind Turbines
Gearbox
Epoxy-Glass
Composite Blades
Electrical Pitch
Drives
Transformer &
Electrical
Doubly-Fed
Generator
Main Shaft &
Bearing
Power Electronic Converter
GE 1.5 MW
77 M Rotor Diameter
50-100 M Tower
98% Availability
Speed 10-20 RPM
Variable Pitch

## Slide 8: Nacelle & Hub components
Rotor main shaft
Pitch drive
Hub
Main bearing
‘Top box’:
low voltage, control…
Generator
Bed Frame
Yaw drives
High-speed coupling
Gearbox
Wind Sensors
GE 1.5 wind turbine
52 metric ton nacelle
35 metric ton rotor
Pitch bearing
Mechanical brake
Yaw bearing
8
Notes: 8
Each rotor blade can be turned using the pitch drive.
The drive train of the WTGS consists of the hub, the rotor shaft, the gearbox, the coupling, and the generator.
This is mounted on the ground frame. The rotor shaft is mounted in the main bearing.
The gearbox and the generator are noise decoupled to minimized the transmission of noise into the tower.
The gear oil is cooled using the oil cooler above a particular temperature.
The generator is cool with the chiller above it. In the so-called "top box" there is a small portion of the control system.
The yaw drives are used to turn the WTGS into the direction of the wind.

## Slide 9
Design of Wind Turbines: Mechanical and Electrical System
Electrical
Generator
Transformer
Down tower Cables
Controls
Top Controller
  Bottom Controller
  Hub Controller
  Sensors
Mechanical
Electrical
Mechanical
Blades & Rotor
  Drive train
  Main Shaft & Gearbox
  Pumps
  Hydraulic
  Motors
  Yaw
Notes: WTG
Muscle that pitches wind-turbine blades comes primarily from hydraulics

## Slide 10: Mechanical system

## Slide 11: Rotor
The assembly of blades, hub, pitch actuators, and spinner are commonly called “The Rotor”

## Slide 12: Blades
Glass Reinforced Polyester blade components:
Airfoil shape and tip design
Skew or twist along length from tip to root
Root & Root Bearing
Chord or Spar
Shell
Notes: Materials
Metals, used on only small-scale turbines due to weight and metal fatigue –Aluminum and Steel
Fiberglass (Prepreg), glass fiber reinforced polyester or epoxy
Carbon Fibers, Kevlar (Aramid)
Wood (Birch)
Paint and surface treatments for corrosion protection

## Slide 13: Blade pitch system
Maintain optimum blade orientation
Safety shut-down system
Electric or hydraulic Controlled
Pitch components mounted inside hub
Independent blade pitch
Controlled via turbine control unit

## Slide 14: Hub & Pitch system
Hub Assembly
Pitch system… critical to safety
  Pitch blades out of the wind
  Maintain rated power
  Shut turbine down
Source: GE energy – 2007 Sandia reliability conference
Source: GE energy – 2007 Sandia reliability conference
14
Notes: The hub is a single die cast unit, used as a structural frame to transmit the torque created from the blades to the main shaft
It houses components such as the pitch actuators, linkage and controller
It is covered by the spinner

## Slide 15: Commercial Pitch Controller

## Slide 16: Yaw Control
Yaw refers to the rotation of the entire wind turbine in the horizontal axis.
Yaw control ensures that the turbine is constantly facing into the wind to maximize the effective rotor area and, as a result, power.
Because wind direction can vary quickly, the turbine may misalign with the oncoming wind and cause power output losses.

## Slide 17: Secondary Braking System Similar to Parking Brake
Credits: Chris Elkinton

## Slide 18
Single-Stage Planetary Gearbox
Internal Gear
Planetary Gear
Sun Gear
Electrical Generator
Armature Coils
Gear Connected to low speed shaft
Credits: Mike Mitsik

## Slide 19: Gearbox and Generator View
Credits: Chris Elkinton

## Slide 20: Electrical systems

## Slide 21: Wind Turbine Generator

## Slide 22: Tower and Power Electronics
Source: GE energy – 2007 Sandia reliability conference
View of 2.5MW tower base
Source; GE Energy
Power conversion… critical to flexibility
  Grid integration and compliance
  Variable speed capability
22
Notes: 22

## Slide 23: The electrical grid

## Slide 24: Generators and converters – function
Design choices?

## Slide 25: Two basic generator types
Synchronous Generator (incl. Permanent Magnet)
Generator speed matches grid (synchronized)
Common in large power generation
Asynchronous (Induction) Generator
Power lags rotational speed of generator
More common in wind turbines

## Slide 26
Fig Gearbox failure
Direct Drive Wind Turbines
Why Direct Drive?
Gearbox problems are responsible for many turbine failures.
Lifetime of the gearboxes sometimes does not reach 5 years.
Its replacement creates cost of up to $200,000 for a 1.5 MW turbine which is more than 10% of the turbine investment cost.
Typical gearboxes are 2-3 stages Planetary gear boxes type

## Slide 27: Directly Rotor-Driven Variable-Speed Generators
Production of synchronous multi-pole generators by Enercon
Direct-drive multi-pole synchronous generator of the Enercon E-30
Generator requires large number of poles to reach the grid frequency that the generator diameter and weight assume unacceptable dimensions

## Slide 28: Turbine Step-Up Transformer
Generation within turbine at low voltage (≤1000 V)
Collection system at medium voltage (10-35 kV)
Oil-Filled Pad-Mount versus Dry-Cast Nacelle Mount
Medium Voltage Cable routings
Delta versus Wye Connections

## Slide 29: Design of MV Collection System

## Slide 30: Wind energy grid integration and operation

## Slide 31: The ERCOT Region
The interconnected electrical system serving most of Texas, with limited external connections
90% of Texas electric load; 75% of Texas land
Load- 71,110 MW peak, August 11, 2016
More than 46,500 miles of transmission lines
16,022 MW wind generation record (instantaneous), December 25, 2016
570+ generation units

## Slide 32: The ERCOT Region Wind Energy Integration
Texas Grid - ERCOT
Wind Generation: Techno-Economic-Policy related impacts in Texas
Addition of new transmission lines-CREZ

## Slide 33: Power systems objectives
Real/Active Power is Balance ensured frequency stability.
Imaginary/Reactive Power is Balance ensures Voltage stability.

## Slide 34: Conclusions
Wind Turbine Conversion Principles: From Wind Energy to Electrical Energy has been covered.
Wind Turbine Mechanical Systems including turbine blades movement and gearboxes covered.
Wind Turbine Electrical Systems including Generator, Power Electronics, Transformers and Lines Covered.
Wind Energy Grid Integration and Operation requirements covered.